## Slide 1: Indian Power Stations O&M Conference IPS 2024
“Quantum leaps in dry fly ash evacuation system to enhance dry fly ash evacuation capacity - An NTPC Darlipali Experience”
Presenter: Raunak Singh Rana
Co-Authors: S. Suresh
Gurpreet Singh Heer
Lukesh Kumar
दर्लीपाली
DARLIPALI
Notes: Mass flow rate calculation, temperature, data,

## Slide 2
Problem Identification
Results & Improvements
Root Cause Analysis & Actions taken
Ash Evacuation Challenges
Presentation Outline

## Slide 3
Ash Evacuation Challenges

## Slide 4
Fly Ash Generated in India – A Report by CEA
SUMMARY OF FLY ASH GENERATION AND UTILIZATION DURING 1ST HALF OF YEAR 2022-23
Ash Evacuation Challenges

## Slide 5
Decreasing Coal Quality
Trend of GCV of coal fired at NTPC Darlipali
Monthly ash content in coal at NTPC Darlipali
Ash Evacuation Challenges

## Slide 6
Catastrophic Failures in Electrostatic Precipitators (ESP) Due to Poor Fly Ash Evacuation
Ash Evacuation Challenges

## Slide 7
Ash Dumping Below Electrostatic Precipitators (ESP) Due to Poor Fly Ash Evacuation at NTPC Darlipali
Ash Evacuation Challenges

## Slide 8
Repercussions of Poor Fly ash Evacuation
Ash Evacuation Challenges
Equipments | Equipment Running & stand by (as per design per unit) | Equipment running to cater poor evacuation (per unit) | Standby availability per unit)
TACs | 3R + 2S | 5 | All TACs i/s – No standby
IACs | 1R + 1S | 2 | All IACs i/s – No standby
FA pipeline | 3R + 3S | 5 | Only 1 line standby
ALV and associated valves (per pass) | 1R + 3S | 2 | Only 2 ALV standby
Notes: Bar chart

## Slide 9
Repercussions of Poor Fly ash Evacuation
Ash Evacuation Challenges

## Slide 10
Repercussions of Poor Fly ash Evacuation
Ash Evacuation Challenges
Notes: Bar chart

## Slide 12
Transport Air Compressor
LDG
Bag Filters
UDG
Equalising valve
BH Blower
Instrument Air header
  Air lock vessel (ALV)
Ash Inlet Valve
Venting Line
Boosting Line
Vacuum pump
Fly ash from ESP Hopper to Buffer Hopper
Orifice
FA line 1,2 to silo
Fluidizing pads

## Slide 13
Problem Identification
Poor Discharge from ALV to HCSD Silo
Poor Evacuation from Buffer Hopper to ALV
Poor Evacuation from ESP to Buffer Hopper

## Slide 14
Root Cause Analysis & Actions taken
Root Cause Analysis & Actions taken

## Slide 15
Root Cause Analysis
Poor Evacuation from ESP to Buffer Hopper
Evacuation with minimum clean Air by throttling the Air intake Valve to 20% (Air is the carrying medium for Ash Conveying)
Frequent jamming of Material Handling Valves
Economizer ash and Coarse Ash collection in the Initial hoppers of ESP due to poor evacuation of ash from Economizer and Duct & APH hoppers
Interruption in Ash evacuation due to high Buffer hopper level

## Slide 16
Actions taken
Poor Evacuation from ESP to Buffer Hopper
Air Intake Valve opening increased to 100%
Scheduled maintenance of MHV Air intake valve minimized the valve jamming
Economizer & APH/Duct hoppers evacuation improved by splitting the discharge lines into Two.
Buffer Hopper Level transmitter mal function problem addressed by shifting the location where the temperature is less

## Slide 17
Eco-Hoppers Original Scheme
Two major problems:
Discharge line choking and overflow from flushing apparatus was observed upon opening KGVs to 100%.
Frequent leakages from MS discharge pipe.
Root Cause Analysis & Actions taken – Case Study
Economizer ash and Coarse Ash collection in the Initial hoppers of ESP
Notes: Bar chart

## Slide 18
Poor Evacuation from ESP to Buffer Hopper
Coarse Ash Collection in ESP Hoppers
Action Taken
Bifurcation of Economizer & APH/Duct Hopper Discharge Header
Original header
Additional Discharge header
Root Cause Analysis & Actions taken – Case Study
Notes: Bar chart

## Slide 19
Root Cause Analysis
Poor Evacuation from Buffer Hopper to ALV
Lack of sufficient Venting-Boosting time
Improper & Frequent change in Ash Filling & Discharge time of Airlock vessel
Idle time in Airlock vessel evacuation sequence.

## Slide 20
Actions taken
Poor Evacuation from Buffer Hopper to ALV
Ash Filling and discharge time into Airlock vessel optimized
Venting-Boosting Time optimized
Idle time eliminated from Airlock vessel evacuation sequence.

## Slide 21
Poor Evacuation from Buffer Hopper to ALV
Improper timings in ALV Filling-Discharge Sequence
Action Taken
Ash Filling and discharge time, Venting and Boosting time into Airlock vessel optimized. Idle time eliminated.
Net Improvement in Ash conveyed per cycle – 30 Tons/Hr/Line
233 s
180 s
15 Cycle
20 Cycle
Root Cause Analysis & Actions taken – Case Study
ALV Filling-Discharge Sequence timer optimization
Notes: Bar chart

## Slide 22
Root Cause Analysis
Poor Discharge from ALV to HCSD Silo
Frequent damage of Fluidizing pads due to high Fluidizing pressure of Air lock vessel
Interruption in Ash conveying as the Silo level was maintaining high due to restriction in HCSD discharge flow
Repeated Conveying Line pressurization & leakages

## Slide 23
Actions taken
Poor Discharge from ALV to HCSD Silo
HCSD Pump speed increased thereby increased the ash transportation from Silo to Ash dyke
Separate header laid & header pressure maintained low thereby avoided the Fluidizing pad damage/passing
Silo Vent fan speed increased from 31000 to 32000 rpm. Number of couplings is FA lines reduced to half.

## Slide 24
Poor Discharge from ALV to HCSD Silo
Frequent damage of ALV Fluidizing pads
Fluidizing air taken from instrument air header (High Pressure) (Pr. ~ 6 Ksc)
No Separate header for Fluidizing air
Root Cause Analysis
Root Cause Analysis & Actions taken – Case Study
Notes: Bar chart

## Slide 25
Poor Discharge from ALV to HCSD Silo
Frequent damage of ALV Fluidizing pads due to high Fluidizing pressure
Action Taken
Separate Fluidizing air header with heater laid & header pressure maintained at 3 Ksc with throttling valve
Root Cause Analysis & Actions taken – Case Study
Notes: Bar chart

## Slide 26
Results & Improvements

## Slide 27
Zero Partial loss on the account of Dry-Ash Evacuation system
Results & Improvements

## Slide 28
Improvement of system Reliability and Availability
Unit 1
Unit 2
Earlier 10 out of 10 TACs and 10 out of 12 FA lines were in service leaving no stand-by equipment.
Now, 2 TACs are stand-by and 5 FA lines are stand-by.
Results & Improvements

## Slide 29
Reduction in APC ---> Saving - INR 89,85,600 (last four months)
Saving of INR 2,69,56,800 (2.7 crores annually)
Reduction in Auxiliary Power Consumption (APC)
Results & Improvements

## Slide 30
Safety and Environment
Before
After
Results & Improvements

## Slide 31
Improvement
of Employee
and workers morale
Results & Improvements