## Slide 2
SSTPS
Asset Fault Prediction through Machine Learning Models
Presented by:
Abhishek Joshi (O&M-C&I)
PRADIP
Go Digital Go Paperless
SAP
Singrauli Super Thermal Power Station

## Slide 3: FLOW OF PRESENTATION
Introduction
Artificial Intelligence and Machine learning
Failure Mode and Effects Analysis (FMEA)
Predictive/Image Analytics - Case study of TDBFP EHTC
Intangible and Tangible Benefits
Advantages

## Slide 4
TRADITIONAL PROGRAMMING V/S MACHINE LEARNING

## Slide 5
LATE FAILURE MODE DISCOVERY
Failure mode discovery
Failure mode creation
No. of outage/partial losses
Too Much Time
Time
Failure

## Slide 6
EARLIER FAILURE MODE DISCOVERY
Failure mode discovery
Failure mode creation
No. of outage/partial losses
Time
Minimized
Time
Failure

## Slide 7
THE “MACHINE LEARNING” APPROACH
Negative Time
(Predictive)
Time
Failure mode discovery
Failure mode creation
No. of outage/partial losses
Failure

## Slide 8: THE “MACHINE LEARNING” APPROACH
Machine Learning Regression models learn the normal behavior of asset from historical data
Each set of measurements of an asset form a ‘Learning Vector’
Model predicts value of each signal of asset using the ML algo.
Anomaly generated on a parameter if difference between predicted value & actual value outside statistical distribution learned by the system
Anomaly generated much before the DCS alarm giving more window for action

## Slide 9: Electro-Hydraulic control of Main Turbine & TDBFP
Electro Hydraulic governing is used to control the opening of Control Valve of Main Turbine and TDBFP based on electrical signal, generated from Speed, Load and Pressure transducer.
Any problem in EHTC circuit may disturb the opening of control valve, thereby causing unit disturbance and may lead to Unit Trip.
Being a complex system, even after proper observation, it is hard to predict EHTC failure.

## Slide 10: Case Study Of EHTC Failure of Unit-6 TDBFP
13th July 2021: U#6 TDBFP-A:
22:30 hrs – Hunting 20 to 30 rpm.
22:42 hrs - Hunting normalized.
23:05 hrs - Hunting started again.
23:10 hrs – Unit Tripped on Drum Level (Severe Hunting).
Observation:
  Sudden increase in EHTC O/P or balance voltage of plunger coil & TD-A failed.
  Balance voltage of coil suddenly varied from -1.0V to 2.5 V.
  Lift oil pressure constant at 4.95 ksc .

## Slide 11: Case Study Of EHTC Failure of Unit-6 TDBFP
Analysis & Investigation:
13th July 2021 15:00 Hrs:
(few hours before tripping)
  Normal Operation
  Sudden change in lift oil pressure
  Resulting change in balance voltage of the coil from -0.5 V to -1.5 V

## Slide 13: Implementation of new Transmitter

## Slide 14: Predictive Modelling using ML

## Slide 15: A Glimpse of AI Algorithm of EHTC Logic at NTPC Singrauli
Adaptive Preset value
Present value
Present value
Present value
LIFT OIL PR
EHC OIL PR.
CONTROL OIL PR
DEVIATION
HIGH
DEVIATION HIGH
DEVIATION HIGH
Preset value
Present value
EHC BALANCE VOLT
DEVIATION HIGH
OR
AND MANY MORE
AND
SEC. OIL PR
AUX. SEC. OIL PR
ROC
ROC
OR
Predictive Alarm Information System
AND MANY MORE
Watch dog Signal/Quality Signal
Adaptive Preset value
Adaptive Preset value

## Slide 16: Case Study Of EHTC Failure of Unit-6 TDBFP-A
19th July 2022: U#6 TDBFP-A:
Hunting observed in TDBFP-A speed
ALARM PROVIDED BY OUR PREDICTIVE SYSTEM
Machine taken into hydraulic immediately
Analysis & Investigation:
Repeat of 13th July 2022 event.
  Coil Balance voltage -1.0 V to 2.5 V
  No significant change in lift oil pressure
Tripping on drum level avoided.

## Slide 17: Predictive and Prescriptive Analytics of Unit-6 TDBFP-B
5th May 2023: U#6 TDBFP-B:
At 16:30 hrs.
TD-B was being taken into EHC after Overhauling.
During Unloading of TD-B for governing characteristics checking, it was observed coil voltage started reducing suddenly.
Alert generated by Predictive Algorithm

## Slide 18: Predictive and Prescriptive Analytics of Unit-6 TDBFP-B

## Slide 19: Predictive and Prescriptive Analytics of Unit-6 TDBFP-B
5th May 2023: U#6 TDBFP-B:
At 20:00 hrs.
TD-B was being again taken into EHC.
During loading of TD-B, it was observed coil voltage started increasing suddenly.
Alert generated by Predictive Algorithm at 20:18 hrs
At 20:55 hrs, EHC malfunctioned.

## Slide 20: Predictive and Prescriptive Analytics of Unit-6 TDBFP-B
24th May 2023: U#6 TDBFP-B:
At 17:30 hrs.
TD-B was again taken into EHC after work by BHEL expert.
Alerts were still being generated by predictive model but they were within limits

## Slide 21: Predictive and Prescriptive Analytics of Unit-6 TDBFP-B
27th May 2023: U#6 TDBFP-B:
At 11:30 hrs.
Alerts generated by predictive model were outside statistical distribution
TD-B was taken out of EHC

## Slide 22: Image Analytics for Diagnosis

## Slide 23: Training Images for Benchmarking – Signature Development
Lift oil _ balance voltage fault
Lift oil _ balance voltage fault
speed fault
Multiple Faults
Normal
Balancing Voltage
Speed
Lift Oil Pressure
Balancing Voltage
Balancing Voltage
Lift Oil Pressure
Speed

## Slide 24: Test Runs for Diagnostics
Instance 01
Speed
Lift Oil Pressure
Balancing Voltage
Speed
Instance 03
Instance 02

## Slide 25: Image Analytics for Diagnosis

## Slide 26: Predictive and Prescriptive Analytics of Unit-6 TDBFP-B
1St August 2023: U#6 TDBFP-B:
At 11:30 hrs.
Alerts generated by prescriptive model with following diagnosis:
Balance position of the pilot valve is getting changed with respect to the speed.
Leakage and spring problem suspected in EHC assembly.
Issues detected in EHC assembly:
Size of the marked assembly was shorter in length.
Mechanical Clearances between pilot and sleeve had increased.

## Slide 27: Predictive and Prescriptive Analytics of Unit-6 TDBFP-B
4th Aug 2023: U#6 TDBFP-B:
At 10:00 hrs.
Finally, TD-B was taken into EHC.
EHC assembly was replaced.
NO alert generated by predictive model till now.

## Slide 28: Why EHC is Critical ?
2022-23 Data on EHC malfunction
1. Unit-5 Dadri Coal : Unit tripped on EHC malfunction( Collins Tx-2 failure).
2. Unit-4 Dadri Coal : Unit tripped on EHC failure(Command and feedback mismatch).
3. Unit-5 Ramagundam : Unit tripped on Collins Tx-1 failure.
4. Unit-4 Dadri Coal : Unit again tripped on Malfunction of EHC system.
5. Unit-1 Simhadri : Unit tripped on EHC problem.
6. Unit-2 Farakka : Unit tripped on EHC malfunction (Collins Tx-2 feedback froze).
7. Unit-3 Bongaigaon : Unit tripped on EHC problem.
8. Unit-1 Simhadri : Unit tripped on EHC malfunction.
If one can predict, one can prevent

## Slide 29: FUTURE POTENTIALS OF THE PROJECT
Automatic capture of relevant DDCMIS data through PI Server to the Predictive Analytics system.
Automatic scheduling of Analysis (00:00 hrs every day).
Access of Analytics result to concerned in control room (Operations, MTP, EEMG)
Application of the tools for other systems such as early detection of BTL etc and final extrapolation to complete process including off-site areas.
Development and deployment of Image Analytics based Diagnostics (Asset Fault Signature) for various critical equipment.

## Slide 30: ADVANTAGES
1
2
3
4
5
Predictive Maintenance
Reduction in Plant outage.
High Return on Investment
Heading Font Size 36
Font Family: Tw Cen MT (Normal)
Content Font Size 14
Font Family: Tw Cen MT (Normal)
Sustainability
Asset health Optimization

## Slide 31: ADVANTAGES
6
7
8
Reliability
Heading Font Size 36
Font Family: Tw Cen MT (Normal)
Content Font Size 14
Font Family: Tw Cen MT (Normal)
Profitability
Safety
9
Scalability

## Slide 32: CONCLUSION

## Slide 33
Thank You