## Slide 1
Cracking of LPT Rotor Groove
Migratory birds at NTPC Dadri
NTPC Rojmal
NTPC Singrauli
NTPC Talcher, Kaniha
Date : 13.02.2024
-by 1K.P. Pradhan, 2S.C. Bhoi, 3A. Mondal
1NTPC SR-HQ, Secunderabad, 2NTPC TSTPS-Talcher Kaniha, 3 NTPC Energy Technology Research Alliance (NETRA)

## Slide 2: Identification of Crack
MPI of LP Turbine free standing blades and Rotor grooves is done in NTPC during OH of units with periodicity of 4 years as per OS guidelines.
The activity for Rotor groove inspection consists of blade removal (de-blading), groove cleaning and magnetic particle inspection.
TSTPS U#3 OH (June, 2023) : Crack observed in one of the LP turbine 5th stage (Generator Side) rotor grooves (no.27) while carrying out MPI
TSTPS U#4 OH (Aug, 2023): All 5th stage rotors grooves (both sides) (124 nos) found to have crack while carrying out MPI.
Crack Location- 5th stage blade groove

## Slide 3: Unit operation details
UNIT # 3
Boiler Light up: September, 2002
Unit Synchronization: January, 2003
Number of starts of unit : approx. 60
Number of operating hours of unit : 164 K hours
UNIT # 4
Boiler light up: July, 2003
Unit Synchronization: October, 2003
Number of starts of unit : approx. 60
Number of operating hours of unit : 158 K hours
Notes: 23

## Slide 4: Crack is Intermittently breaking (not continuous), Spread across the length of Steeple-1 (starting from ~20 mm from the edge)
Nature of Crack in U#3 LPT Rotor
Start of crack

## Slide 5
CRACK

## Slide 6: Dye Penetrant Testing and Fluorescent penetrant Testing in Groove No -27
CRACK

## Slide 7: PAUT Comparison between: Groove No: 27 (With Suspected Crack) & Groove No: 28 (Healthy)
Healthy Groove
Groove with crack
PAUT of steeple by NETRA

## Slide 8: Grinding of Crack
Grinding Depth 2mm Approx
Grinding was done 0.1 to 0.2 mm each time with MPI to check the crack
Crack was completely removed after approx. 2 mm grinding

## Slide 9: Tools used for grinding
Small milling tools
Miniature pneumatic grinder

## Slide 10: Ensuring crack elimination
Complete removal of crack was ensured through MPI

## Slide 11: Cracks identified in LP Rotor 5th Stages of Unit#4

## Slide 12: Location of crack : Pressure side ( first serration)
Crack
Crack
Total number of cracks found in the LP rotor : 124 cracks (one crack in each rotor groove).
Location of Cracks : L-1 steeples
Cracks in 35 grooves found to have propagated to the sides

## Slide 13
Crack in Rotor groove cross checked using UT

## Slide 14: Grinding of crack
Crack was ground using grinding tools up to 5mm depth
However, crack could not be removed

## Slide 15
Typical Locations of Disc Rim Cracking

## Slide 16: Schematic of axial-entry fir tree groove design in LP rotor with typical cracking locations shown

## Slide 17: Cursory look into SCC
Although Stress Corrosion Cracking (SCC) can occur in many locations of steam turbine, most of them initiate at LP disc rim, rotor groove or blade attachment area.
Usually power plants operating more than 15 years are susceptible to this failure mechanism. If SCC happens, especially in rotor groove, it has a major influence on steam turbine life.
Because of the complexity of crack growth behavior, it is difficult to estimate the remaining life of the rotor with cracks found.

## Slide 18: SCC Mechanism
In LP turbine section, cracking on rotor due to SCC has been most prevalent in fir-tree or inverted fir-tree groove designs but it also has been noted in other designs such as finger type design.
Cracks initiate from surface especially around the notches of the grooves and propagate across the steeples.
Corrosion induced cracks are brittle, usually branching, and may be either trans-granular or inter-granular depending upon the material composition, stress levels, and corrosive environment.

## Slide 19: Stress Corrosion Cracking Mechanism
Failure mechanism is a function of stress intensity, rotor material, and steam environment so that the probability of occurrence is higher in the longer last stage blades when the moisture of condensation begins to form. Figure below shows an example of SCC found on LP rotor groove
Figure: Example of Stress Corrosion Cracking on LP rotor groove crack and microstructure of crack examined by replication

## Slide 20: Properties of SCC
Crack propagation rate from SCC can be divided into 3 regions as a function of applied stress intensity factor (KI) which are dependent, constant, and approaching final failure.
In the first phase, SCC can only propagate when stress intensity at rotor groove exceeds the threshold of the crack growth stress intensity (KISCC).
When KI<KISCC, indication may be in the form of localized corrosion and its magnitude or degree of severity becomes less significant.

## Slide 21: Properties of SCC
For the second phase, crack growth rate is assumed to be constant and independent from applied load or KI. We call this region “plateau” region.
After stable growth phase, in Stage-III, SCC may change its mode to Low Cycle Fatigue (LCF) or High Cycle Fatigue (HCF). The crack is accelerated into unstable regime hence fast fracture will soon come.

## Slide 22: Critical Crack depth
Once SCC is found, actual crack dimensions had been recorded for reference. In addition, the two most crucial things to be determined are critical crack depth and crack growth rate.
The critical crack depth (acr) can be calculated by Finite Element Analysis (FEA) software where acr is the minimum crack depth that the applied stress intensity factor (KI) exceeds the material toughness (KIC).
Note that KI is the function of assumed crack geometry or flaw shape and KIC depends on material properties.

## Slide 23: Factors affecting crack
Factors | Mechanism
Root Causes | SCC is caused by a combination of High surface stresses, A susceptible material, Operational and shutdown environments. Design-related root causes are the most important and prevalent. They include High surface tensile stresses and stress concentrations, and Use of high strength materials.
Fractography | SCC cracks of low alloy steels often initiate from pits and propagate intergranularly with branching. The initial part of the crack can be corroded and filled with magnetite. Depending on the ratio of the steady and cyclic stresses, the disc cracks can be a mixture of intergranular and transgranular cracking

## Slide 24: Three Components of Turbine Stress Corrosion and Corrosion Fatigue Cracking in Turbines.
Factors affecting crack

## Slide 25: Factors affecting crack
 | Factors | Mechanism
MATERIAL | Materials | All low alloy steels used for LP turbine rotors and discs are susceptible to SCC and CF in numerous turbine environments including pure water and wet steam. The strongest material factor influencing SCC is yield strength. At higher yield strength, SCC crack growth rate can be several orders of magnitude higher than for lower yield strength materials.
STRESS | Vibratory stresses | Vibratory stresses reduce the life when the flaws reach a sufficient size that fatigue becomes a dominant mechanism.
 | Cyclic stresses | Cyclic stresses are caused by: Turbine startups and shutdowns (high cyclic stresses), Turbine and blades ramping through critical speeds at which some components are in resonance (high amplitude, high frequency)

## Slide 26: Factors affecting crack
Environment | Factors | Mechanism
 | Shutdown environment | Sodium hydroxide is the most severe SCC environment encountered in steam turbines. The sources of NaOH include Malfunctioning condensate polishers and makeup systems and Improper control of phosphate in boiler water chemistry combined with high carryover.
 | Steam chemistry | Operating outside of recommended steam purity limits for long periods of time; sometimes caused by organic acids from elevated concentrations of steam impurities (particularly of chloride, sodium, and sulfate) and the resulting deposition and concentration by evaporation of moisture are underlying causes of corrosion fatigue. High steam sodium or cation conductivity may indicate conditions that can lead to rapid accumulation of deposits and concentrated liquid films on blade surfaces.
 | Pitting | When corrosive deposits are present, pitting during unprotected layup can be faster than pitting during operation. This is because during the layup, there can be 100 percent relative humidity and there is oxygen present. At high stresses, above the elasticity limit of the material, pitting is enhanced through the mechanism identified as stress induced pitting

## Slide 27: Way forward
Inspection of U#3 LPT rotor in next OH for checking further development of crack if any.
Root Cause analysis for such crack initiation
Allowable crack size?
Repair of U#4 rotor

## Slide 28
Dovetails are especially prone to fatigue cracking and Stress-Corrosion Cracking (SCC), which is defined as the growth of cracks in a corrosive environment. If left unchecked, SCC can lead to unexpected failure of normally ductile metals subjected to tensile stress, such as is the case in turbines.
The cracking of interest here is typically small and concentrated near dovetail hooks. Conventional eddy current pencil probes and Penetrant Testing (PT) were used for a number of years with very limited success. The specific geometries of dovetails make inspection with these methods unreliable, if at all possible.
Inspecting Turbine Dovetails with Eddy Current Array Technology

## Slide 29
Of the two dovetail parts, inspecting the female portion has proven the most time-consuming and demanding. Inspection usually involves using slow, complex, and costly robots.
Furthermore, because there are almost as many dovetail designs as there are turbines, a one-size-fits-all solution such as a flexible design is virtually unthinkable, especially while wanting to preserve the level of precision necessary to effectively characterize minute cracks.
This application therefore calls for a solution that can scan female dovetails in a single pass and designed to match the dovetail’s profile.
Inspecting Turbine Dovetails with Eddy Current Array Technology

## Slide 30
Because dovetails vary greatly in shape and size, they usually require a custom solution. The Eddy Current Array (ECA) technology in the probe remains nonetheless the same.
To scan a wide inspection area, ECA technology uses multiplexing. That is, several individual coils are grouped together in one probe and excited sequentially to eliminate interference from mutual inductance. The coils are designed to have the necessary impedance and penetration level for accurate inspection.
Moreover, the coils are mounted inside a thin (0.25 mm or 9.8 mil), spring-loaded and durable membrane, guaranteeing constant contact with the dovetail. The shape of the probe also makes it very stable and easy to handle, eliminating the need for expensive robotic solutions
MultiScan MS5800 multitechnology acquisition unit
Inspecting Turbine Dovetails with Eddy Current Array Technology

## Slide 31: The Challenge
Efficiently inspect turbine dovetails for minute cracking, extending the life of aging equipment.
Dovetails are prone to fatigue cracking and stress corrosion cracking (SCC)
Cracking of interest is typically:
    Small
    Concentrated at dovetail hooks
Conventional EC pencil probes and PT have very limited success because the specific geometries of dovetails make these methods unreliable, sometimes impossible.

## Slide 32: The Challenge
Female dovetails are the most challenging. Inspections usually:
  Require much time and effort
  Involve slow, complex, and costly robots
Dovetail designs are multifarious
  One-size-fits-all solution almost impossible
Need for a solution that can scan female dovetails in a single pass, designed to match the dovetail’s profile.

## Slide 33: The Solution
ECA probes perfectly profiled to match dovetail geometries.

## Slide 34: The Solution
To scan a wide inspection area, ECA technology uses multiplexing.
    Several individual coils are grouped together in one probe and excited sequentially to eliminate interference from mutual inductance.
    Coils designed to have the necessary impedance and penetration level for accurate inspection.
Coils mounted inside thin (0.25 mm/9.8 mil), spring-loaded, durable membrane.
    Constant contact with dovetail guaranteed.
Very stable and easy to handle
    No need for expensive robotic solutions.

## Slide 35: The Solution
Dovetail probe equipped with precision encoders
    Allow locating and sizing length of defects in space when analyzing 2D and 3D C-scans with the Magnifi® high-performance acquisition and analysis software.
  Magnifi is also capable of computerized record keeping and reporting
  Great advantages over PT.

## Slide 36
Driving the dovetail probe is the Ectane® — a compact, rugged, battery-operated, and portable ECA data acquisition unit with an integrated multiplexer.

## Slide 37: The Solution
Actual testing on dovetail profiles demonstrates that detection capabilities are:
    As much as 0.38 mm (0.015 in.) in depth
    As short as 0.76 mm (0.030 in.) in length

## Slide 38: The Benefits
This dovetail inspection solution has several advantages over others:
    Custom solution shaped to specific dovetail profiles
    Custom solution designed to target specific “hot spots” or entire dovetail profile
    Rapid, single-pass scan of regions of interest
    No harsh chemicals or hazardous waste
    Easy to handle — no need for expensive robotic solutions
    Easier interpretation with C-scan imaging capabilities
    Full computerized data recording and archiving

## Slide 40: Authors
Shri Krushna Prasad Pradhan
Sr. Manager, QA&I
NTPC SRHQ, Secunderabad
Dr. Avijit Mondal, PhD
Sr. Manager, NETRA
NTPC Energy Technology Research Alliance (NETRA)
Greater NOIDA-201301
Shri Susil Chandra Bhoi
DGM, Mech Maintenance-Turbine
NTPC TSTPS, Talcher Kaniha