## Slide 1
BARH SUPER THERMAL POWER PROJECT
/ntpc1
/ntpcltd1
/ntpclimited
/Company/ntpc
/ntpclimited
Follow us on:
Maintenance practices for enhancing asset management in EHV substation
Parag Chatterjee
Senior Manager, NTPC Barh

## Slide 2
ZERO FORCED OUTAGE

## Slide 3: CONTENTS
Asset Management
Safety & Interlocking Design
Case Studies
New Technologies

## Slide 4: Overview of 400 kV substation (SCADA HMI)

## Slide 5
Remote asset management by predictive maintenance

## Slide 6
Current sharing across bays

## Slide 7
Current sharing across bays before and after maintenance
Ir (TOTAL) | 354 Amps | Iy (TOTAL) | 374 Amps | Ib (TOTAL) | 367Amps
Ir (Main Bay 20) before rectification) | 0 | Iy (Main Bay 20) before rectification) | 0 | Ib (Main Bay 20) before rectification) | 198 Amps
Ir (Main Bay 20) after rectification) | 177 Amps | Iy (Main Bay 20) after rectification) | 180 Amps | Ib (Main Bay 20) after rectification) | 198 Amps
Ir (Tie Bay 19) Initial contribution | 354 Amps | Iy (Tie Bay 19) Initial contribution | 374 Amps | Ib (Tie Bay 19) Initial contribution | 169 Amps
Ir (Tie Bay 19) Final Contribution | 177 Amps | Iy (Tie Bay 19) Final Contribution | 194 Amps | Ib (Tie Bay 19) Final Contribution | 169 Amps

## Slide 8
Alarm -Annunciation Dashboard

## Slide 9
CASE STUDY 1
ALARM & ANNUNCIATION DASHBOARD
Unit in running condition
4-652 Main breaker of Unit
4-552 Tie breaker of Unit & ICT
4-452 Main Breaker of ICT
Unit in tripped condition
4-652 Main breaker of Unit-OFF
4-552 Tie breaker of Unit & ICT-OFF
4-452 Main Breaker of ICT- ON
4-552 conducted in OFF condition
Unit in tripped condition
4-652 Main breaker of Unit-OFF
4-552 Tie breaker of Unit & ICT-OFF
4-452 Main Breaker of ICT- OFF
TIE LBB operated

## Slide 10
Fault finding in 400 kV Breaker pole

## Slide 11
CASE STUDY 2
Events recorded in SCADA
Disturbance recorded in standalone DRPC

## Slide 12
CASE STUDY 2
SCADA dashboard displayed class-A 87GT differential protection
Standalone DRPC connected to remote Generator protection Relays in CCR enabled to analyse the disturbance
Root cause of the problem identified in GT turret CT cable

## Slide 13
LINE EARTH SWITCH INTERLOCKING
Clarity in communication to remote desk operator
Additional safety feature
Local closing of E/S enabled only when line voltage < 30% (P-N)

## Slide 14
LINE ISOLATOR INTERLOCKING

## Slide 15
CVT VOLTAGE MONITORING

## Slide 16
FREQUNCY DOMAIN SPECTROSCOPY
Non-invasive technique
Calculates moisture in solid insulation
Inference on residual life assessment of EHV transformers and bushings

## Slide 17
FREQUNCY DOMAIN SPECTROSCOPY

## Slide 18
Automated Thermography
Acoustic Partial Discharge
Online Differential Current Monitoring
WAY AHEAD

## Slide 19
Q&A!