## Slide 1
Way of Sustainable Ash Utilisation : Fine Fly Ash Collection and Transportation through BTAP wagons

## Slide 2
RIHAND
Category-C
AU Compliance as per MoEF&CC Notifications: Category C : (As ash utilization < 60% in FY 2021-22) 5-year compliance cycle | No minimum ash utilization % requirement in FY 2022-23 & FY 2023-24 Minimum 80 % ash utilization in FY 2024-25, FY 2025-26 & FY 2026-27 Overall Avg. 100 % ash utilization at the end of 5 Years compliance cycle ie FY 2026-27
Current AU Progress | FY 2022-23 | FY 2022-23 till Last Month | FY 2023-24 (Projected) | Projected upto Last Month in FY 2023-24 | FY 2023-24 till Dec 23
Ash Utilization (%) | 52.90 | 52.11 | 76.54 | 72.71 | 70.02
Target to avoid EC in Comp. Cycle- 121.48 %
EC(Comp. cycle) as per previous FY AU trend- 950.5 Cr.
EC applicable in FY 23-24 at current rate of AU (Cr) | Asking rate to achieve 80% AU in FY 23-24 (%) / (MT)
NA | 108 % / 11178.9 MT
Projected
Actual
Asking Rate
Asking Rate (MT/Day) wrt station Target
Avenue
Roads
Mine
Brick Ind.
Land Dev
NI /Agg. /BA
0
0
0
556
237
1180
1111
1558.4
0
667
153.3
2200
5556
5657
6699
694
552
1100
Cement & Ind.
Total
8583
8157.7
11179
Chart: 
| 2016-17 | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 (till Dec'23)
Ash Utilization % | 15.47 | 31.04 | 37.1 | 43.18 | 52.02 | 59.28 | 52.9 | 70.02
Legacy Ash Stock as on 31.12.2023: 28.58 LCM (w.e.f 01.04.2022)

## Slide 3: Avenue Wise Ash Utilization Plan & Utilization Trend
BTAP: FY 20-21: - 09 Rakes, FY 21-22: - 45 Rakes, FY 22-23: - 48 Rakes & FY 23-24(Running): - 46 Rakes
5 YEAR AU Plan of Rihand* |  |  |  |  | 
Considering Avg Rihand Ash Production in 05 years: 37 LMT Per Annum |  |  |  |  | 
Avenues | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27
Wasteland Dev | 2.33 | 4 | 11 | 12 | 12
Mine Filling | 0 | 0 | 6 | 10 | 15
Cement Industry | 1.66 | 2.5 | 4 | 5 | 8
Brick etc. | 1.14 | 2 | 3 | 4 | 5
Road Projects | 13.83 | 20 | 10 | 10 | 12
Ash Mound | 0 | 0 | 0 | 0 | 0
Aggregate / Sand/Geo Polymer / Cenosphere | 2.4 | 2.4 | 1.25 | 1.0 | 2.0
Fine Fly Ash | - | 0 | 2.0 | 3.0 | 4.0
Total (LMT/%) | 21.36 | 30.9 | 37.25 | 45 | 58
 | 52.90% | 83.51% | 101% | 122% | 157%
Dry Ash Utilization in last 04 Years |  |  | 
Financial Year | Ash Generated (LMT) | Ash Utilised (LMT) | Ash Utilization (%)
2019-20 | 10.4 | 1.394 | 13.40
2020-21 | 10.45 | 2.45 | 23.45
2021-22 | 9.88 | 2.46 | 24.89
2022-23 | 10.76 | 2.80 | 26.00
2023-Till Dec’ 23 | 8.35 | 2.53 | 30.29

## Slide 4
One more product is Classified (fine fly) Ash:
AMCC.
Overview
Classified ash is the ash which conforms to IS 3812 (part1) in term of fineness or as per customer requirement.
It is either collected through Classifier or through modification of existing collection system in separate Silo from second / third … field onwards.
Separate guideline for issue/sale of classified ash has been issued by AMCC.

## Slide 5: Classified Ash Avenues
Ready Mix Concrete (RMC)
Demand of high Blaine size ash in Cement Industry
FINE FLY ASH
Mixing of Fine fly ash in Concrete upto 35 %
Export of Classified Ash as per international standard
In aggregate production

## Slide 6: NTPC Ash Collection systems
100 % Dry Ash system which have normally 02 buffer hopper for each pass like Mouda.
Ejector along with dry system which have 01 buffer hopper in each pass like Ramagundam.
Wetting head along with dry system which have 01 buffer hopper in each pass like Vindhyachal.
Flushing apparatus/Ejector along with dry system which have 01 buffer hopper in each pass like Sipat.
NTPC Fly ash evacuation system may be majorly categorized as

## Slide 7
Wetting Unit
Air Washer
Vacuum Bkr
Seal Box
FAHP
Header V/V
1
8
2
3
4
5
6
7
ESP Hopper
Ash Evacuation Line
Vacuum Line
Vacuum Pump
Bag Filter
Vent Fan
Rotary Feeder
Ash Conditioner
Ash Silo
Fluidizing Blower
Closed Bulker
Open Truck
Air In Take V/V
MHV
Inst air for purging bags
DRY Ash Inlet valve
WET Ash Inlet valve
Collector Tank
Slurry Trench
SCHEMATIC DIAGRAM OF FINE FLY ASH SYSTEM
2nd Field onwards
Bag Filter
Transfer
Hopper
Buffer Hopper
Transporter
Receiver
Fluidizing Blower
Equalizing Line
To ESP Duct
To Wet System

## Slide 8
Technical Specification and Analysis
Particle Size: >80 Micron 40 to 80 Micron
Analysis of Fly Ash | % by weight
Greater than 40 microns | 20
30-40 microns | 10
20-30 microns | 14
10-20 microns | 24
Less than 10 microns | 32
Total | 100
COAL ANALYSIS | 
GCV | 3778
Carbon % | 39.75
Ash % | 30.01
Moisture % | 7.94
Volatile matter % | 22.3
COAL MILL FINENESS ANALYSIS |  |  | 
MILL | 50 | -100 | -200
LIMIT | 1% | 90% | 70%
A | 0.6 | 90 | 68
B | 0.5 | 92 | 72
C | 0.4 | 94 | 72
D | 0.5 | 91 | 71
E | 0.2 | 96 | 77
F | 0.4 | 92 | 73
G | 0.5 | 91 | 72
H | 0.4 | 93 | 68
J | 0.3 | 95 | 76
FLY ASH DENSITY ANALYSIS |  |  | 
ESP PASS |  |  | 
A | B | C | D
0.95 | 1 | 0.85 | 0.9
LIMIT:0.75 gm/cc |  |  | 
Unburnt Carbon Analysis |  | 
Area | Fly Ash | Bottom Ash
value (%) | 0.2 | 0.6
Limit (%) | 1.0 | 1.5
Fly Ash Collection in ESP Hopper for 500 MW unit |  |  |  |  |  |  | 
HR | Coal fired TPH | % Ash in Coal |  | Total Ash Produced (TPH) | Bottom Ash (20%) | Fly Ash ESP(80%) | Ash per pass (TPH)
 | 300 | 30% |  | 90 | 18 | 72 | 18
24 | 7200 | 30% |  | 2160 | 432 | 1728 | 432
ESP Field wise Ash collection |  |  |  |  |  |  | 
Field No |  |  | % Distribution of Ash | % of Ash / pass |  | Ash T/pass / hr | 
1 |  |  | 64 | 64 |  | 11.52 | 
2 |  |  | 20.3 | 20.3 |  | 3.65 | 
3 |  |  | 8.4 | 8.4 |  | 1.51 | 
4 |  |  | 3.96 | 3.96 |  | 0.71 | 
5 |  |  | 1.8 | 1.8 |  | 0.32 | 
6 |  |  | 0.85 | 0.85 |  | 0.15 | 
7 |  |  | 0.45 | 0.45 |  | 0.08 | 
8 |  |  | 0.24 | 0.24 |  | 0.04 | 
Total |  |  | 100 | 100 |  | 18 | 
Total One Day Ash Collection Per Pass |  |  |  |  |  | 432 | 
Total one Day Four Pass Ash Collection |  |  |  |  |  | 1728 | 

## Slide 9
Procedure for Coarse ash(1st hopper) and Fine ash (2nd onward hopper) collection through deferent mode:
  Mode-1: ESP Hopper no. 1of all branch lines of any Pass can be evacuated for 02 Cycles thorough Wetting head and taken to ash dyke. The same process can be repeated for all passes.
  Mode-2: ESP 2nd hopper to 8th hopper of all branch lines of any Pass can be evacuated thorough Buffer hopper and subsequently it can be transported to silo (identified for fine fly ash) through fly ash conveying line. The same process can be repeated for all passes with respective Buffer hoppers and fly ash conveying line .
Initially, all the operation has to be performed on Manual mode of selection on trial basis, however for continues collection of fine fly it can be done through change in C&I logic.
*- All numbers mentioned is for reference only, any buffer & silo combination may be used.
Procedure

## Slide 10
Header V/V
1
8
2
3
4
5
6
7
MHV
2nd Field onwards
1st
Field
Flexible Operation of Fine Fly Ash evacuation System
Flexible Operation of Fine Fly Ash evacuation was started with 02 cycles of 1st field and one cycle of 2nd field onwards ( Hopper no 2 to 8).
2nd field onwards can be considered fine with ash collection quantity of collection of 622 MT per day.
Flexible Operation of Ash evacuation system |  |  |  | 
Load |  | Shut off Vacuum |  | 
coal |  | Line Vacuum |  | 
Mode of Operation | Evacuation Cycle | Hopper No. | Time Taken (Minutes) | Cycle Time
Wet | 2 | Line-1 to 4 ( Hopper-1) | 15 | 70
 |  | Line-1 to 4 ( Hopper-1) | 8 | 
C/O |  | wet to Dry Mode | 10 | 
Dry | 1 | Line-1 to 4 ( Hopper-2 to 8) | 27 | 
C/O |  | Dry to Wet Mode | 10 | 
Wet | 2 | Line-1 to 4 ( Hopper-1) | 20 | 96
 |  | Line-1 to 4 ( Hopper-1) | 12 | 
C/O |  | wet to Dry Mode | 8 | 
Dry | 1 | Line-1 to 4 ( Hopper-2 to 8) | 48 | 
C/O |  | Dry to Wet Mode | 8 | 
Wet | 2 | Line-1 to 4 ( Hopper-1) | 26 | 104
 |  | Line-1 to 4 ( Hopper-1) | 12 | 
C/O |  | wet to Dry Mode | 8 | 
Dry | 1 | Line-1 to 4 ( Hopper-2 to 8) | 50 | 
C/O |  | Dry to Wet Mode | 8 | 
Wet | 2 | Line-1 to 4 ( Hopper-1) | 33 | 115
 |  | Line-1 to 4 ( Hopper-1) | 18 | 
C/O |  | wet to Dry Mode | 8 | 
Dry | 1 | Line-1 to 4 ( Hopper-2 to 8) | 48 | 
C/O |  | Dry to Wet Mode | 8 | 
Wet | 2 | Line-1 to 4 ( Hopper-1) | 30 | 103
 |  | Line-1 to 4 ( Hopper-1) | 12 | 
C/O |  | wet to Dry Mode | 8 | 
Dry | 1 | Line-1 to 4 ( Hopper-2 to 8) | 45 | 
C/O |  | Dry to Wet Mode | 8 | 
Wet | 2 | Line-1 to 4 ( Hopper-1) | 23 | 94
 |  | Line-1 to 4 ( Hopper-1) | 15 | 
C/O |  | wet to Dry Mode | 8 | 
Dry | 1 | Line-1 to 4 ( Hopper-2 to 8) | 40 | 
C/O |  | Dry to Wet Mode | 8 | 
Fly Ash Collection in ESP Hopper for 500 MW unit |  |  |  |  |  |  | 
HR | Coal fired TPH | % Ash in Coal | Total Ash Produced (TPH) | Bottom Ash (20%) | Fly Ash ESP(80%) | Ash per pass (T) | 
 | 300 | 30% | 90 | 18 | 72 | 18 | 
24 | 7200 | 30% | 2160 | 432 | 1728 |  | 
Field wise Ash collection |  |  | ESP Pass wise Ash collection |  |  |  | 
Field No | % of Ash | Ash T/hr | Time (Hr) | One pass | Two pass | Three pass | Four pass
1 | 64 | 0.00 | 1 | 6.48 | 12.96 | 19.44 | 25.92
2 | 20.3 | 3.65 | 2 | 12.96 | 25.92 | 38.88 | 51.84
3 | 8.4 | 1.51 | 3 | 19.44 | 38.88 | 58.32 | 77.76
4 | 3.96 | 0.71 | 4 | 25.92 | 51.84 | 77.76 | 103.68
5 | 1.8 | 0.32 | 5 | 32.40 | 64.80 | 97.20 | 129.60
6 | 0.85 | 0.15 | 6 | 38.88 | 77.76 | 116.64 | 155.52
7 | 0.45 | 0.08 | 7 | 45.36 | 90.72 | 136.08 | 181.44
8 | 0.24 | 0.04 | 8 | 51.84 | 103.68 | 155.52 | 207.36
 | 100.00 | 6.48 | 9 | 58.32 | 116.64 | 174.96 | 233.28
 |  |  | 10 | 64.80 | 129.60 | 194.40 | 259.20
 |  |  | 11 | 71.28 | 142.56 | 213.84 | 285.12
 |  |  | 12 | 77.76 | 155.52 | 233.28 | 311.04
 |  |  | 13 | 84.24 | 168.48 | 252.72 | 336.96
 |  |  | 14 | 90.72 | 181.44 | 272.16 | 362.88
 |  |  | 15 | 97.20 | 194.40 | 291.60 | 388.80
 |  |  | 16 | 103.68 | 207.36 | 311.04 | 414.72
 |  |  | 17 | 110.16 | 220.32 | 330.48 | 440.64
 |  |  | 18 | 116.64 | 233.28 | 349.92 | 466.56
 |  |  | 19 | 123.12 | 246.24 | 369.36 | 492.48
 |  |  | 20 | 129.60 | 259.20 | 388.80 | 518.40
 |  |  | 21 | 136.08 | 272.16 | 408.24 | 544.32
 |  |  | 22 | 142.56 | 285.12 | 427.68 | 570.24
 |  |  | 23 | 149.04 | 298.08 | 447.12 | 596.16
 |  |  | 24 | 155.52 | 311.04 | 466.56 | 622.08
NTPC Rihand started collecting fine fly Ash from 2nd field onwards.

## Slide 11
However on testing of this collected ash by 45 µm sieve analysis, value was 21-22 in comparison to accepted value of 16 for fine ash categorization for accepted industry norms.
Report received on 09.12.2023 with 21 percent retention on 45-micron sieve.

## Slide 12
Procedure for Coarse ash(1st hopper) and Fine ash (2nd onward hopper) collection through deferent mode:
  Cycle-01
    Mode-1: ESP Hopper no. 1of all branch lines of any Pass can be evacuated thorough Wetting head and taken to ash dyke. The same process can be repeated for all passes.
    Mode-2: ESP 2nd hopper to 8th hopper of all branch lines of any Pass can be evacuated thorough Buffer hopper and subsequently it can be transported to silo (identified for fine fly ash) through fly ash conveying line. The same process can be repeated for all passes with respective Buffer hoppers and fly ash conveying line .
  Cycle-02
    Mode-1: ESP Hopper no. 1&2 of all branch lines of any Pass can be evacuated thorough Wetting head and taken to ash dyke. The same process can be repeated for all passes.
    Mode-2: ESP 3nd hopper to 8th hopper of all branch lines of any Pass can be evacuated thorough Buffer hopper and subsequently it can be transported to silo (identified for fine fly ash) through fly ash conveying line. The same process can be repeated for all passes with respective Buffer hoppers and fly ash conveying line .
Procedure with alternate hopper

## Slide 13
Fly Ash Collection in ESP Hopper for 500 MW unit |  |  |  |  |  |  | 
HR | Coal fired TPH | % Ash in Coal | Total Ash Produced (TPH) | Bottom Ash (20%) | Fly Ash ESP(80%) | Ash per pass (T) | 
 | 300 | 30% | 90 | 18 | 72 | 18 | 
24 | 7200 | 30% | 2160 | 432 | 1728 |  | 
Field wise Ash collection |  |  | ESP Pass wise Ash collection |  |  |  | 
Field No | % of Ash | Ash T/hr | Time (Hr) | One pass | Two pass | Three pass | Four pass
1 | 64 | 0 | 1 | 4.65 | 9.31 | 13.96 | 18.61
2 | 20.3 | 2 | 2 | 9.31 | 18.61 | 27.92 | 37.22
3 | 8.4 | 1.51 | 3 | 13.96 | 27.92 | 41.88 | 55.84
4 | 3.96 | 0.71 | 4 | 18.61 | 37.22 | 55.84 | 74.45
5 | 1.8 | 0.32 | 5 | 23.27 | 46.53 | 69.80 | 93.06
6 | 0.85 | 0.15 | 6 | 27.92 | 55.84 | 83.75 | 111.67
7 | 0.45 | 0.08 | 7 | 32.57 | 65.14 | 97.71 | 130.28
8 | 0.24 | 0.04 | 8 | 37.22 | 74.45 | 111.67 | 148.90
 | 100.00 | 4.65 | 9 | 41.88 | 83.75 | 125.63 | 167.51
 |  |  | 10 | 46.53 | 93.06 | 139.59 | 186.12
 |  |  | 11 | 51.18 | 102.37 | 153.55 | 204.73
 |  |  | 12 | 55.84 | 111.67 | 167.51 | 223.34
 |  |  | 13 | 60.49 | 120.98 | 181.47 | 241.96
 |  |  | 14 | 65.14 | 130.28 | 195.43 | 260.57
 |  |  | 15 | 69.80 | 139.59 | 209.39 | 279.18
 |  |  | 16 | 74.45 | 148.90 | 223.34 | 297.79
 |  |  | 17 | 79.10 | 158.20 | 237.30 | 316.40
 |  |  | 18 | 83.75 | 167.51 | 251.26 | 335.02
 |  |  | 19 | 88.41 | 176.81 | 265.22 | 353.63
 |  |  | 20 | 93.06 | 186.12 | 279.18 | 372.24
 |  |  | 21 | 97.71 | 195.43 | 293.14 | 390.85
 |  |  | 22 | 102.37 | 204.73 | 307.10 | 409.46
 |  |  | 23 | 107.02 | 214.04 | 321.06 | 428.08
 |  |  | 24 | 111.67 | 223.34 | 335.02 | 446.69
Flexible Operation of Ash evacuation system |  |  |  | 
Load |  | Shut off Vacuum |  | 
coal |  | Line Vacuum |  | 
Mode of Operation | Evacuation Cycle | Hopper No. | Time Taken (Minutes) | Cycle Time
Wet | 1 | Line-1 to 4 ( Hopper-1 &2 ) | 19 | 70
C/O |  | wet to Dry Mode | 10 | 
Dry | 1 | Line-1 to 4 ( Hopper-3 to 8) | 31 | 
C/O |  | Dry to Wet Mode | 10 | 
Wet | 2 | Line-1 to 4 ( Hopper-1) | 20 | 88
C/O |  | wet to Dry Mode | 8 | 
Dry | 2 | Line-1 to 4 ( Hopper-2 to 8) | 52 | 
C/O |  | Dry to Wet Mode | 8 | 
Wet | 3 | Line-1 to 4 ( Hopper-1 &2 ) | 37 | 100
C/O |  | wet to Dry Mode | 9 | 
Dry | 3 | Line-1 to 4 ( Hopper-3 to 8) | 46 | 
C/O |  | Dry to Wet Mode | 8 | 
Wet | 4 | Line-1 to 4 ( Hopper-1 &2 ) | 40 | 128
C/O |  | wet to Dry Mode | 8 | 
Dry | 4 | Line-1 to 4 ( Hopper-3 to 8) | 71 | 
C/O |  | Dry to Wet Mode | 9 | 
Wet | 5 | Line-1 to 4 ( Hopper-1 &2 ) | 52 | 106
C/O |  | wet to Dry Mode | 8 | 
Dry | 5 | Line-1 to 4 ( Hopper-3 to 8) | 37 | 
C/O |  | Dry to Wet Mode | 9 | 
Wet | 6 | Line-1 to 4 ( Hopper-1 &2 ) | 44 | 107
C/O |  | wet to Dry Mode | 9 | 
Dry | 6 | Line-1 to 4 ( Hopper-3 to 8) | 46 | 
C/O |  | Dry to Wet Mode | 8 | 
Hence ash collected from ESP 3rd field onwards can be considered as fine ash. But quantity of ash collected from 3rd field onwards is mere 270 MT per day and storing this fine ash for longer period may create settling of ash since fine ash is very hygroscopic. However if ash from second field is also included in alternate evacuation cycle than quantity of ash comes to 445 MT per day. Once again ash was collected by operating evacuation system flexibly with inclusion of 2nd field in alternate cycle. Sample of this collected ash was tested by 45 µm sieve analysis, value was 16 thus adhering to accepted industry norms.
Fine fly ash again started with combination of 2nd & 3rd field
Flexible Operation of Fine Fly Ash evacuation System

## Slide 14
This fine ash was collected for 07 days and accumulated in silo with partial unloading (25-35MT per day) into truck from silo to maintain flowability of ash. Later ash was loaded and kept in one BTAP wagon for 07 days. This BTAP wagon was unloaded successfully in our silo after 07 days.
Days | Load (MW) | Coal fired TPH | Two pass Fine Fly ash collection | Collection Time (Hr) | Ash collection in Silo | Maintain flowability of ash | Ash Accumulated in silo
1 | 500 | 301 | 9.34 | 7 | 65 | 30 | 35
2 | 490 | 295 | 9.15 | 8 | 73 | 30 | 43
3 | 498 | 280 | 8.69 | 8 | 69 | 30 | 39
4 | 502 | 302 | 9.37 | 9 | 84 | 30 | 54
5 | 514 | 330 | 10.24 | 8 | 82 | 30 | 52
6 | 494 | 312 | 9.68 | 9 | 87 | 30 | 57
7 | 501 | 299 | 9.27 | 8 | 74 | 30 | 44
Total Ash collection |  |  |  |  | 536 | 210 | 326
Test report established that we were able to achieve 16 % retention on 45 micron sieve.
07 days trial operation results

## Slide 15
Fine fly ash was loaded into 01 BTAP wagon which was then kept in MGR to simulate the real time conditions(Assuming min. seven days are required for transporting Ash from Rihand to NCR region via BTAP rakes)
We were able to successfully unload the loaded BTAP wagon after 07 days. With this we became the first Power plant in the country to do successful trail of loading storing & unloading of Fine Fly ash
Trial of Loading, Storing & Unloading in BTAP wagons

## Slide 16: BEST PRACTICES
Best/next practice | Implemented from | Remarks | Benefits/gains
Evacuation & transportation of fine fly ash through BTAP Wagons | Trials completed successfully | 3rd Station in NTPC to Start Fine FlyAsh Collection while 1st Station in NTPC to conduct trial through BTAP wagons | Improved ash utilization. Cost effective transportation to long distances. Enables direct blending with OPC Can be used directly at site of construction

## Slide 17
Why Fine Fly transportation via BTAP wagons is a game changer
BTAP SFTO registration charges | Procurement of BTAP wagons (159 Nos.) | MGR Augmentation | Infrastructure Augmentation
₹ 7 crore | ₹ 67 crore | ₹ 7 crore | ₹ 3 crore
Total Expenditure : 84 Crores |  |  | 
EXPECTED PRICE EX. RIHAND | ANNUAL FINE FLYASH GENERATION | EXPECTED REVENUE
₹ 200 PER TON | 4 LAKH MT | ₹ 8 crore
EXPECTED REVENUE BY SALE OF FINE FLY ASH
COST OF ESTABLISHING FINE FLY ASH COLLECTION & TRANSPORTATION VIA BTAP WAGONS
Industries | Distance from Rihand (Kms) | Present Cost by industries (by road), Rs./MT | Transportation cost through Rail, Rs./MT | Considering Rs 200 paid to Rihand for Fine fly ash. Savings to cement Indutries(Rs./MT)
Satna Cement | 297 | 1000 | 607 | 193
Prism Cement | 281 | 950 | 628 | 222
KJS Cement | 303 | 1000 | 568 | 232
Maihar Cement | 299 | 1000 | 568 | 232
ACC Kymore, | 327 | 1200 | 480 | 520
Cost Benefit Analysis for Cement Industries