## Slide 1
By
Dr. Dipravath Kumar Seth
Deputy Manager (O&M Chemistry)
NTECL/ NTPC Vallur
OPTIMIZATION OF DM PLANT REGENERATION PROCESS- TO ENSURE DM WATER AVAILABILITY

## Slide 2
De-Mineralisation Plant
DEGASSER
ACF
WAC
SAC
WBA
SBA
MB
DM-ST
D/G P/P
Filter water Header
DG blower

## Slide 3
Cl
WBA
SBA
A-
SiO2
A-
SiO2
SiO2
Mixed Bed Vessel
SiO2
< 200ppb
SiO2
SiO2
< 20ppb
ANION vessel IN SERVICE
Air and Carbon di Oxide (CO32-)
Water from SAC
De gasser Tank
AIR
De gasser
P/P
A- = Cl-, SO42-, NO3-
H+
H+
H+
H+
H+
H+, A-, CO32-,
SiO2

## Slide 4
Cation resin vessel removes all type of cationic
impurities.
5% HCl required for Cation resin regeneration.
Anion resin vessel removes all type of anionic
impurities and Silica.
5% NaOH required for Anion resin regeneration.
De-Mineralisation Plant

## Slide 5: SBA REGENERATION PROCESS
Cl
WBA
SBA
Caustic (approx. 50% NaOH) Metering Tank
5% NaOH solution
Power Water
2% NaOH solution
Pump
To N-Pit
DOWN FLOW WATER

## Slide 6: NORMAL OPERATION Stg II DMP
Normal OBR for ST#2 DM Plant = 1600m3
Design flow for one DM stream = 130m3/hr
Operation time for one stream = 12.5 hrs
Regeneration time = 6 hrs
Average Station consumption per day = 2800-3100m3
HEALTHY DM WATER STOCK TO BE MAINTAINED AROUND 6000 TO 6500m3.

## Slide 7: DM water consumption pattern
Chart: 
| 2017-2018 | 2018-2019 | 2019-2020 | 2020-2021 | 2021-2022 | 2022-2023
Consumption (m3) | 2826 | 2549 | 2885 | 3012 | 3135 | 3865
Year wise Daily Average DM water Consumption
Consumption (m3)

## Slide 8: PROBLEMS FACED
Deterioration of raw water quality
Increasing trend of make-up (DM water)
Premature exhaustion of SBA : DM output decrease (Shooting of SiO2)
Increase in frequency of regeneration : High Caustic Consumption
More effluent generation
Attrition loss of resin : Resin loosing efficiency
More outage time due to regeneration: Less production time

## Slide 9
DG Blower
DG Tank
SBA
DG Blower
DG Blower
DG Tank
SBA
As per design CO2 limit at DGT O/L- 5 ppm
CO2 Found – 174 ppm
High CO2 ingress in WBA
Extra load on WBA
Decrease in ion exchange capacity of WBA
DG Tower Inefficiency
Initiative taken
Found CO2 – 200 ppm

## Slide 10: SUMMARY OF PROBLEM
With 50%
efficiency

## Slide 11: UNDERSTANDING..
Cl
WBA
SBA
Insoluble SiO2
Caustic (Approx. 50%) Metering Tank
5% NaOH solution
Power Water
Pump
To N-Pit
Soluble SiO2
Normal regeneration process
Insoluble SiO2
2% NaOH
Ingressed CO32-
: Soluble silica converted to insoluble silica

## Slide 12
LEARNING PROCESS..

## Slide 13
SUMMARY OF STUDY:
Ingression of high CO2 into WBA: formation of carbonic acid
Decrease in the pH of the regenerant: Insoluble silica dumped in WBA
Ingression of high CO2 into WBA: extra ionic load on WBA
Extra load on SBA: SBA got fully exhausted
SBA consumes almost entire amount of caustic for regeneration: WBA regeneration hampered
Despite of using freshly prepared Caustic solution we are getting low output.

## Slide 14
Remedy
Use of 4 times caustic
Result
Getting better OBR than before
Demerit
Increased production cost of DM water.
Outcome of study

## Slide 15: Brain STORMING…

## Slide 16
Cl
WBA
SBA
Insoluble SiO2
Caustic (Approx.50 %) Metering Tank
5% NaOH solution
Power Water
Pump
To N-Pit
To N-Pit
Low pH of
regenerant
Insoluble SiO2
2% NaOH: Optimum pH
WORK OUT

## Slide 17
RESULT
Chart: Specific Caustic Consumption
| Design | Last 6 month | Dec-21 | Jan-22 | Feb-22 | Mar-22 | Next 6 month
 | 0.137 | 0.128 | 0.345 | 0.515 | 0.414 | 0.397 | 0.141

## Slide 18
COST BENEFIT
Chart: Cost of Specific Chemical consumption in Rs/M3
| Design | Last 6 month | Dec-21 | Jan-22 | Feb-22 | Mar-22 | Next 6 month
 | 12.33 | 11.52 | 31.05 | 46.35 | 37.26 | 35.73 | 12.69
Average monthly production
at St#2 DM Plant 50000 M3
Cost of caustic used in Jan 2022 = 24.3 Lac
Cost of caustic used in next 6 month = 6.3 Lac
(after modification)
Savings due to lesser
caustic spent pm = ~18 lac

## Slide 19: SHARING OF EXPERIENCE..

## Slide 20: RCA to Permanent Solution
R&M of DG Tower
Replacement of DG Blower
Poor Performance of DG Tower
CO2 level at DG Tank O/L < 4 PPM.
Presently no issue of Insoluble silica

## Slide 21
Safer tank level achieved.
Caustic consumption almost
normalised.
OBR restored to 1000 m3 compared to 500 m3
during critical hours
CONCLUSION

## Slide 22
Acknowledgements
NTPC IPS 2024
Mr. B. S. Rao (AGM Chem NTPC Farakka)
Mr. Kajjal Pramanik (Co-other NTPC Farakka)

## Slide 24
ANY QUESTIONS?

## Slide 25
Chart: DM water production and Consumption
| 44348 | 44378 | 44409 | 44440 | 44470 | 44501 | 44531 | 44562 | 44593 | 44621 | 44652 | 44682 | 44713
Production | 114744 | 124485 | 135250 | 130345 | 146745 | 105529 | 111622 | 116671 | 101917 | 120774 | 130074 | 124857 | 126327
Consumption | 116319 | 120624 | 133900 | 129250 | 143132 | 104475 | 111151 | 114378 | 100791 | 113097 | 91830 | 124904 | 122404